## Slide 1
<number>
Training Session on Energy Equipment
Steam Distribution and Utilization
Presentation from the
“Energy Efficiency Guide for Industry in Asia”
www.energyefficiencyasia.org
Notes: <number>
TO THE TRAINER
This PowerPoint presentation can be used to train people about the basics of steam. The information on the slides is the minimum information that should be explained. The trainer notes for each slide provide more detailed information, but it is up to the trainer to decide if and how much of this information is presented also.
Additional materials that can be used for the training session are available on www.energyefficiencyasia.org under “Energy Equipment” and include:
Textbook chapter on this energy equipment that forms the basis of this PowerPoint presentation but has more detailed information
Quiz – ten multiple choice questions that trainees can answer after the training session
Workshop exercise – a practical calculation related to this equipment
Option checklist – a list of the most important options to improve energy efficiency of this equipment
Company case studies – participants of past courses have given the feedback that they would like to hear about options implemented at companies for each energy equipment. More than 200 examples are available from 44 companies in the cement, steel, chemicals, ceramics and pulp & paper sectors

## Slide 2: Training Agenda: Steam
<number>
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities

## Slide 3: Introduction
<number>
Transport and provision of energy
Benefits
  Efficient and economic to generate
  Easy to distribute
  Easy to control
  Easily transferred to the process
  Steam plant easy to manage
  Flexible
Alternatives are hot water and oils
Why do we use steam?
Notes: <number>
Steam today is an integral and essential part of modern technology. Without it, our food, textile, chemical, medical, power, heating and transport industries could not exist or perform as they do.
Steam provides a means of transporting controllable amounts of energy from a central, automated boiler house, where it can be efficiently and economically generated, to the point of use. Therefore as steam moves around a plant it can equally be considered to be the transport and provision of energy.
For many reasons, steam is one of the most widely used commodities for conveying heat energy. Its use is popular throughout industry for a broad range of tasks from mechanical power production to space heating and process applications. Reasons for using steam include:
  Steam is efficient and economic to generate
  Steam can easily and cost effectively be distributed to the point of use
  Steam is easy to control
  Energy is easily transferred to the process
  The modern steam plant is easy to manage
  Steam is flexible
The alternatives to steam include water and thermal fluids such as high temperature oil. Each method has its advantages and disadvantages

## Slide 4: Introduction
<number>
Molecule: smallest of any compound
Water = H2O
  two hydrogen atoms (H)
  one oxygen atom (O)
Three physical states
  solid: ice
  liquid: water
  vapour: steam
What is steam?
Notes: <number>
A better understanding of the properties of steam may be achieved by understanding the general molecular and atomic structure of matter and applying this knowledge to ice, water and steam
A molecule is the smallest amount of any element or compound substance still possessing all the chemical properties of that substance which can exist. Molecules are made up of even smaller particles called atoms, which define the basic elements such as hydrogen and oxygen
One such compound is represented by the chemical formula H2O, having molecules made up of two atoms of hydrogen and one atom of oxygen.
Most mineral substances can exist in the three physical states (solid, liquid and vapour), which are referred to as phases. In the case of H2O, the terms ice, water and steam are used to denote the three phases respectively.

## Slide 5: Introduction
<number>
Triple point: ice, water and steam in equilibrium
Ice: molecules can only vibrate
Water: molecules are free to move but close together
Steam: molecules are furthest apart
What is steam?
Notes: <number>
All the three phases of a particular substance can only coexist in equilibrium at a certain temperature and pressure, and this is known as its triple point. The triple point of H2O, where the three phases of ice, water and steam are in equilibrium, occurs at a temperature of 273.16 K and an absolute pressure of 0.006112 bar. This pressure is very close to a perfect vacuum. If the pressure is reduced further at this temperature, the ice, instead of melting, sublimates directly into steam.
Ice. In ice, the molecules are locked together in an orderly lattice type structure and can only vibrate. In the solid phase, the movement of molecules in the lattice is a vibration about a mean bonded position where the molecules are less than one molecular diameter apart. Heat that breaks the lattice bonds to produce the phase change while not increasing the temperature of the ice, is referred to as enthalpy of melting or heat of fusion.
Water. In the liquid phase, the molecules are free to move, but are still less than one molecular diameter apart due to mutual attraction, and collisions occur frequently. More heat increases molecular agitation and collision, raising the temperature of the liquid up to its boiling temperature
Steam. As the temperature increases and the water approaches its boiling condition, some molecules attain enough kinetic energy to reach velocities that allow them to momentarily escape from the liquid into the space above the surface, before falling back into the liquid. As the water is heated to its boiling point, bubbles of steam form within it and rise to break through the surface. When the number of molecules leaving the liquid surface is more than those re-entering, the water freely evaporates. At this point it has reached boiling point or its saturation temperature, as it is saturated with heat energy. If the pressure remains constant, adding more heat does not cause the temperature to rise any further but causes the water to form saturated steam.

## Slide 6: Introduction
<number>
Steam saturation curve
What is steam?
Steam Saturation Curve (Spirax Sarco)
Superheated steam
Sub-saturated water
Notes: <number>
At atmospheric pressure the saturation temperature is 100°C. However, if the pressure is increased, this will allow the addition of more heat and an increase in temperature without a change of phase. Therefore, increasing the pressure effectively increases both the enthalpy of water, and the saturation temperature. The relationship between the saturation temperature and the pressure is known as the steam saturation curve
Water and steam can coexist at any pressure on this curve, both being at the saturation temperature. Steam at a condition above the saturation curve is known as superheated steam:
  Temperature above saturation temperature is called the degree of superheat of the steam
  Water at a condition below the curve is called sub-saturated water.

## Slide 7: Introduction
<number>
Enthalpy of water (hf)
  Heat required to raise temperature from 0oC to current temperature
Enthalpy of evaporation (hfg)
  Heat required to change water into steam at boiling point
Enthalpy of saturated steam (hg)
  Total energy in saturated steam
What is steam - Enthalpy
hg = hf + hfg
Notes: <number>
Enthalpy of water, liquid enthalpy or sensible heat (hf) of water. This is the heat energy required to raise the temperature of water from a datum point of 0°C to its current temperature. At this reference state of 0°C, the enthalpy of water has been arbitrarily set to zero. The accepted terms these days are liquid enthalpy or enthalpy of water.
Enthalpy of evaporation or latent heat (hfg). This is the amount of heat required to change the state of water at its boiling temperature, into steam. It involves no change in the temperature of the steam/water mixture, and all the energy is used to change the state from liquid (water) to vapour (saturated steam).
Enthalpy of saturated steam, or total heat of saturated steam. This is the total energy in saturated steam, and is simply the sum of the enthalpy of water and the enthalpy of evaporation.

## Slide 8: Introduction
<number>
Dry saturated steam: T = boiling point
Steam: mixture of water droplets and steam
Dryness fraction (x) is 0.95 if water content of steam = 5%
Actual enthalpy of evaporation = dryness fraction X specific enthalpy hfg
What is steam – Dryness fraction
Notes: <number>
Steam with a temperature equal to the boiling point at that pressure is known as dry saturated steam. However, to produce 100 percent dry steam in an industrial boiler designed to produce saturated steam is rarely possible, and the steam will usually contain droplets of water.
In practice, because of turbulence and splashing, as bubbles of steam break through the water surface, the steam space contains a mixture of water droplets and steam.
If the water content of the steam is 5 percent by mass, then the steam is said to be 95 percent dry and has a dryness fraction of 0.95.
The actual enthalpy of evaporation of wet steam is the product of the dryness fraction (x) and the specific enthalpy (hfg) from the steam tables. Wet steam will have lower usable heat energy than dry saturated steam. Actual enthalpy of evaporation = hfg x. Wet steam will have lower usable heat energy than dry saturated steam.

## Slide 9: Introduction
<number>
What is steam?
Temperature Enthalpy Phase Diagram (Spirax Sarco)
Notes: <number>
The data provided in the steam tables can also be expressed in a graphical form. The figure illustrates the relationship between the enthalpy and the temperature at various different pressures, and is known as a phase diagram.
Click once. A to B. As water is heated from 0°C to its saturation temperature, its condition follows the saturated liquid line until it has received all of its liquid enthalpy, hf.
Click once. B to C.If further heat continues to be added, it then changes phase to saturated steam and continues to increase in enthalpy while remaining at saturation temperature, hfg. As the steam/water mixture increases in dryness, its condition moves from the saturated liquid line to the saturated vapour line. Therefore at a point exactly halfway between these two states, the dryness fraction (x) is 0.5. Similarly, on the saturated vapour line the steam is 100 percent dry. Once it has received all of its enthalpy of evaporation, it reaches the saturated vapour line.
Click once. C to D. If it continues to be heated after this point, the temperature of the steam will begin to rise as superheat is imparted. The saturated liquid and saturated vapour lines enclose a region in which a steam /water mixture exists - wet steam. In the region to the left of the saturated liquid line only water exists, and in the region to the right of the saturated vapour line only superheated steam exists.
Click once. The point at which the saturated liquid and saturated vapour lines meet is known as the critical point. As the pressure increases towards the critical point the enthalpy of evaporation decreases, until it becomes zero at the critical point. This suggests that water changes directly into saturated steam at the critical point. The critical point is the highest temperature at which a liquid can exist. Any compression at constant temperature above the critical point will not produce a phase change.

## Slide 10: Introduction
<number>
Steam should be available
In correct quantity
At correct temperature
Free from air and incondensable gases
Clean (no scale / dirt)
Dry
Steam quality
Notes: <number>
Steam should be available at the point of use:
In the correct quantity to ensure that a sufficient heat flow is provided for heat transfer
At the correct temperature and pressure, or performance will be affected
Free from air and incondensable gases which act as a barrier to heat transfer
Clean, as scale (e.g. rust or carbonate deposit) or dirt have the effect of increasing the rate of erosion in pipe bends and the small orifices of steam traps and valves
Dry, as the presence of water droplets in steam reduces the actual enthalpy of evaporation, and also leads to the formation of scale on the pipe walls and heat transfer surface.

## Slide 11: Training Agenda: Steam
<number>
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities

## Slide 12: Steam Distribution System
<number>
Link between steam generator and point of use
Steam generator
  Boiler
  Discharge from co-generation plant
Boilers use
  primary fuel
  exhaust gases
What is the steam distribution system?
Notes: <number>
The steam distribution system is the essential link between the steam generator and the steam user. There are various methods to carry steam from a central source to the point of use. The central source might be a boiler house or the discharge from a co-generation plant. The boilers may burn primary fuel, or be waste heat boilers using exhaust gases from high temperature processes, engines or even incinerators.

## Slide 13: Steam Distribution System
<number>
Typical steam circuit
(Spirax Sarco)
Notes: <number>
An understanding of the basic steam circuit or ‘steam and condensate loop’ is required
Note to the trainer: a detailed description is in the chapter. Below are the summarized points only
As steam condenses in a process, flow is induced in the supply pipe.
The steam generated in the boiler must be conveyed through main pipes, or 'steam mains‘ and then smaller branch pipes.
Heat is transferred from the steam to the pipe, so the pipework will begin to transfer heat to the air.
Steam on contact with the cooler pipes will begin to condense immediately. On start-up of the system, the condensing rate will be at its maximum and is commonly called the ‘starting load’. Once the pipework has warmed up, the condensing rate is minimal and commonly called the ‘running load’.
The resulting condensation (condensate) falls to the bottom of the pipe and will then have to be drained from various strategic points in the steam main.
When the valve on the steam pipe serving an item of steam using plant is opened, steam flowing from the distribution system enters the plant and again comes in contact with cooler surfaces. The steam then transfers its energy in warming up an equipment and product (starting load), and, when up to temperature, continues to transfer heat to the process (running load).
There is now a continuous supply of steam from the boiler.
More water (and fuel to heat this water) is supplied to the boiler to make up for the water which has previously been evaporated into steam. The condensate formed in both the steam distribution pipework and in the process equipment is a convenient supply of useable hot boiler feedwater.

## Slide 14: Steam Distribution System
<number>
Steam pressure influenced by many factors
Steam loses pressure in distribution pipework
Advantages of high pressure steam
  Increased thermal storage capacity of boiler
  Smaller bore steam mains required
  Less insulation of smaller bore steam mains
Reduce steam pressure at point of use
Pressure and steam
Notes: <number>
The distribution pressure of steam is influenced by a number of factors, but is limited by:
  The maximum safe working pressure of the boiler
  The minimum pressure required at the plant
As steam passes through the distribution pipework, it will inevitably lose pressure due to:
  Frictional resistance within the pipework
  Condensation within the pipework as heat is transferred to the environment.
  Therefore allowance should be made for this pressure loss when deciding upon the initial distribution pressure.
A kilogram of steam at a higher pressure occupies less volume than at a lower pressure. It follows that, if steam is generated in the boiler at high pressure and also distributed at a high pressure, then the size of the distribution mains will be smaller than that for the same heat load. Generating and distributing steam at higher pressure offers three important advantages:
  The thermal storage capacity of the boiler is increased, helping it to cope more efficiently with fluctuating loads, minimizing the risk of producing wet and dirty steam.
  Smaller bore steam mains are required, resulting in lower capital cost, for materials such as pipes, flanges, supports, insulation and labour.
  Smaller bore steam mains cost less to insulate.
Having distributed at a high pressure, it will be necessary to reduce the steam pressure to each zone or point of use in the system in order to correspond with the maximum pressure required by the application. Local pressure reduction to suit individual plant will also result in drier steam at the point of use.

## Slide 15: Steam Distribution System
<number>
Pipes
Drain points
Branch lines
Strainers
Filters
Separators
Most important components
Steam traps
Air vents
Condensate recovery system
Insulation
Notes: <number>
We will now explain the most important components of a steam distribution system

## Slide 16: Steam Distribution System
<number>
Pipe material: carbon steel or copper
Correct pipeline sizing is important
Oversized pipework:
  Higher material and installation costs
  Increased condensate formation
Undersized pipework:
  Lower pressure at point of use
  Risk of steam starvation
  Risk of erosion, water hammer and noise
Size calculation: pressure drop or velocity
1. Pipes
Notes: <number>
Pipe material: Pipes for steam systems are commonly manufactured from carbon steel to ANSI B 16.9 Al06. The same material may be used for condensate lines, although copper tubing is preferred in some industries. For high temperature superheated steam mains, additional alloying elements, such as chromium and molybdenum, are included to improve tensile strength and creep resistance at high temperatures. Typically, pipes are supplied in 6-meter lengths.
Pipeline sizing: The objective of the steam distribution system is to supply steam at the correct pressure to the point of use. Pipeline sizing is an important factor.
Oversized pipework means:
  Pipes, valves, fittings, etc. will be more expensive than necessary.
  Higher installation costs will be incurred, including support work, insulation, etc.
  For steam pipes a greater volume of condensate will be formed due to the greater heat loss. This in turn means that either more steam trapping is required or wet steam is delivered to the point of use.
Undersized pipework means:
  A lower pressure may only be available at the point of use. This may hinder equipment performance due to only lower pressure steam being available.
  There is a risk of steam starvation.
  There is a greater risk of erosion, water hammer and noise due to the inherent increase in steam velocity.
The required pipeline size can be calculated based on pressure drop and velocity. Note to the trainer: if time allow you can use the chapter to explain how each of these calculation methods work

## Slide 17: Steam Distribution System
<number>
Pipeline layout: 1 m fall for every 100 m
1. Pipes
(Spirax Sarco)
Notes: <number>
The European Standard EN45510, Section 4.12 states that whenever possible, steam mains should be installed with a fall of not less than 1:100 (1 m fall for every 100 m run), in the direction of the steam flow.
This slope will ensure that gravity, as well as the flow of steam, will assist in moving the condensate towards drain points where the condensate may be safely and effectively removed

## Slide 18: Steam Distribution System
<number>
Ensures that condensate can reach steam trap
Consideration must be give to
  Design
  Location
  Distance between drain points
  Condensate in steam main at shutdown
  Diameter of drain pipe
2. Drain points
Notes: <number>
The drain point must ensure that the condensate can reach the steam trap.
Careful consideration must be given to
  the design of the drain points
  Location of the drain points
  Distance between drain points. The amount of condensate formed in a large steam main under start-up conditions is sufficient to require the provision of drain points at intervals of 30m to 50m, as well as natural low points such as at the bottom of rising pipework.
  Condensate remaining in a steam main at shutdown, when steam flow ceases. Gravity will ensure that the water (condensate) will run along sloping pipework and collect at low points in the system. Steam traps should therefore be fitted to these low points.
  Diameter of the drain pipe (discussed on next slides)

## Slide 19: Steam Distribution System
<number>
2. Drain points
Trap Pocket too small (Spirax Sarco)
Notes: <number>
This figure shows a 15 mm drain pipe connected directly to the bottom of a main.
Although the 15 mm pipe has sufficient capacity, it is unlikely to capture much of the condensate moving along the main at high speed. (Point at the blue condensate in the main and the drain pipe underneath). In normal operation, steam may flow along the main at speeds of up to 145 km/h, dragging condensate along with it.
This arrangement will therefore be ineffective.

## Slide 20: Steam Distribution System
<number>
2. Drain points
Properly Sized Trap Pocket (Spirax Sarco)
Notes: <number>
A more reliable solution for the removal of condensate is shown in the Figure. The trap line should be at least 25 to 30 mm from the bottom of the pocket for steam mains up to 100 mm, and at least 50 mm for larger mains. This allows a space below for any dirt and scale to settle. Such dirt and scale can easily be removed if the bottom of the pocket is fitted with a removable flange or blowdown valve.

## Slide 21: Steam Distribution System
<number>
3. Branch lines
Take steam away from steam main
Shorter than steam mains
Pressure drop no problem if branch line < 10 m
A Branch Line (Spirax Sarco)
Notes: <number>
Branch lines are normally much shorter than steam mains. As a general rule, therefore, provided the branch line is not more than 10 metres in length, and the pressure in the main is adequate, it is possible to size the pipe on a velocity of 25 to 40 m/s, and not to worry about the pressure drop

## Slide 22: Steam Distribution System
<number>
Branch line connections
  Top: driest steam
  Side or bottom: accept condensate and debris
3. Branch lines
(Spirax Sarco)
Notes: <number>
Branch line connections taken from the top of the main line, carry the driest steam as can be seen on the figure
(Click once). If connections are taken from the side, or even worse from the bottom as shown on the right figure, they can accept the condensate and debris from the steam main. The result is very wet and dirty steam reaching the equipment, which will affect performance in both the short and long term.

## Slide 23: Steam Distribution System
<number>
Drop leg: low point in branch line
3. Branch lines
Drop Leg Supplying Steam fo a Heater (Spirax Sarco)
Notes: <number>
Low points will also occur in branch lines.
(Click once) The most common is a drop leg close to an isolating valve or a control valve as shown in the figure.
Condensate can accumulate on the upstream side of the closed valve, and then be propelled forward with the steam when the valve opens again –
(Click once) consequently a drain point with a steam trap set is good practice just prior to the strainer and control valve.

## Slide 24: Steam Distribution System
<number>
Sometime steam runs across rising ground
Condensate should run against steam flow
3. Branch lines
Reverse Gradient on Steam Main (Spirax Sarco)
Notes: <number>
There are many occasions when a steam main must run across rising ground, or applications where the contours of the site make it impractical to lay the pipe with the 1:100 fall. In these situations, the condensate must be encouraged to run downhill and against the steam flow.
Good practice is to size the pipe on a low steam velocity of not more than 15 m/s, to run the line at a slope of no less than 1:40, and install the drain points at not more than 15 meter intervals (see Figure 13). The objective is to prevent the condensate film on the bottom of the pipe increasing in thickness to the point where droplets can be picked up by the steam flow.

## Slide 25: Steam Distribution System
<number>
Purpose
  Stop scale, dirt and other solids
  Protect equipment
  Reduce downtime and maintenance
Fitted upstream of steam trap, flow meter, control valve
Two types: Y-type and basket type
4. Strainers
Notes: <number>
In steam and condensate systems, damage to plant is frequently caused by pipeline debris such as scale, rust, jointing compound, weld metal and other solids, which may find their way into the pipeline system.
Strainers are devices which arrest these solids in flowing liquids or gases, and protect equipment from their harmful effects, thus reducing downtime and maintenance. A strainer should be fitted upstream of every steam trap, flow meter and control valve.
Strainers can be classified into two main types according to their body configuration; namely the Y-type and the basket type. Typical examples of these types of strainers can be seen in Figure 14.

## Slide 26: Steam Distribution System
<number>
Y-Type strainers
Handles high pressures
Lower dirt holding capacity: more cleaning needed
4. Strainers
(Spirax Sarco)
Notes: <number>
For steam, a Y-type strainer is the usual standard and is almost universally used.
Its body has a compact cylindrical shape that is very strong and can handle high pressures of up to 400 bar g. The use of strainers at these pressures is however complicated by the high temperatures associated with the steam at this pressure; and subsequently exotic materials such as chrome-molybdenum steel have to be used.
Y-type strainers have a lower dirt holding capacity than basket strainers, which means that they require more frequent cleaning.

## Slide 27: Steam Distribution System
<number>
Y-Type strainers
4. Strainers
(Spirax Sarco)
Notes: <number>
Y-type strainers in horizontal steam or gas lines should be installed so that the pocket is in the horizontal plane. This stops water collecting in the pocket, helping to prevent water droplets being carried over, which can cause erosion and affect heat transfer processes.
(Click once) On liquid systems however, the pockets should point vertically downwards.
(Click once) Although it is advisable to install strainers in horizontal lines, this is not always possible, and they can be installed in vertical pipelines if the flow is downwards, in which case the debris is naturally directed into the pocket (Figure 15b).
Installation is not possible with upward flow, as the strainer would have to be installed with the opening of the pocket pointing downwards and the debris would fall back down the pipe.

## Slide 28: Steam Distribution System
<number>
Basket type strainers
Less pressure drop
Larger dirt holding capacity
Only for horizontal pipelines
Drain plug to remove condensate
4. Strainers
(Spirax Sarco)
Notes: <number>
The basket type or pot type strainer is characterized by a vertically orientated chamber, typically larger than that of a Y-type strainer.
Size for size, the pressure drop across a basket strainer is less than that across the Y-type as it has a greater free straining area, which makes the basket type strainer the preferred type for liquid applications. As the dirt holding capacity is also greater than in Y-type strainers, the basket type strainer is also used on larger diameter steam pipelines.
Basket type strainers can only be installed in horizontal pipelines, and for larger, heavier basket strainers, the base of the strainer needs to be supported.
When basket type strainers are used on steam systems, a significant amount of condensate may be formed. Consequently, strainers designed for use in steam systems usually have a drain plug, which can be fitted with a steam trap to remove the condensate.
Next we will discuss strainer screens, but this figure already illustrates a screen fitted into a strainer. (Point at the screen on the figure before moving on to the next slide)

## Slide 29: Steam Distribution System
<number>
Strainer screens
Perforated screens
  Holes punched in flat sheet
  Large holes
  Removes large debris
Mesh screens:
  Fine wire into mesh arrangement
  Small holes
  Removes small solids
4. Strainers
Example of a 3-mesh Screen (Spirax Sarco)
Notes: <number>
Strainer screens assist in removing solids.
There are two types of screens used in strainers:
Perforated screens. These are formed by punching a large number of holes in a flat sheet of the required material using a multiple punch. Perforated screens are only suitable for removing general pipe debris.
Mesh screens. Fine wire is formed into a grid or mesh arrangement. This is then commonly layered over a perforated screen, which acts as a support cage for the mesh. They are used to remove smaller particles, which would otherwise pass through a perforated screen. Mesh screens are usually specified in terms of ‘mesh’; which represents the number of openings per linear inch of screen, measured from the centerline of the wire. The figure shows a 3-mesh screen

## Slide 30: Steam Distribution System
<number>
Other strainer options
Magnetic inserts: remove iron/steel debris
Self cleaning strainers
  Mechanical: scraper or brush
  Backwashing: reverse flow direction
Temporary strainers: equipment protection during start-ups
4. Strainers
Notes: <number>
Magnetic Inserts: A magnetic insert may be placed in a basket type strainer in order to remove small iron or steel debris..
Self Cleaning Strainers: There are number of different types of self-cleaning strainer, which enable the build up of debris on the screen to be removed without shutting down the plant. The cleaning process can be initiated either manually or automatically; furthermore, strainers that are automatically cleaned can usually be set to clean either on a periodic basis, or when the pressure drop across the strainer increases. The most common types are:
  Mechanical type self-cleaning strainers, which use some form of mechanical scraper or brush, which is raked over the screen surface.
  Backwashing type strainers, which reverse the direction of flow through the screen.
Temporary Strainers: Temporary strainers are designed for protection of equipment and instrumentation during start-up periods. The strainer is usually installed between a set of flanges for an initial period after a new plant has been installed.

## Slide 31: Steam Distribution System
<number>
Consists of sintered stainless steel filter element
Remove smallest particles
  Direct steam injection – e.g. food industry
  Dirty stream may cause product rejection – e.g. paper machines
  Minimal particle emission required from steam humidifiers
  Reduction of steam water content
5. Filters
Notes: <number>
A filter used in a steam system typically consists of a sintered stainless steel filter element.
Filters are used to remove smaller particles than strainers, for example, in the following applications:
When there is direct injection of steam into a process, which may cause contamination of the product. Example: In the food industry, and for the sterilization of process equipment in the pharmaceutical industry.
Where dirty steam may cause rejection of a product or process batch due to staining or visible particle retention. Example: Sterilizers and paper/board machines.
Where minimal particle emission is required from steam humidifiers. Example: Humidifiers used in a “clean” environment.
For the reduction of the steam water content, ensuring a dry, saturated supply.

## Slide 32: Steam Distribution System
<number>
Choose correct size due to large pressure drop
Do not exceed flow rate limits
For steam applications
  Fit separator upstream to remove condensate
  Fit Y-type strainer upstream to remove large particles
Identify when cleaning needed
  Pressure gauges
  Pressure switch
5. Filters
Notes: <number>
The fine porous nature of the filter element will create a large pressure drop across the filter than that associated with the same size strainer; this must be given careful consideration when sizing such filters.
In addition filters are easily damaged by excessive flow rates, and the manufacturers’ limits should not be exceeded.
When the filter is used in steam applications, a separator should be fitted upstream of the filter to remove any droplets of condensate held in suspension. In addition to improving the quality of the steam, this will prolong the life of the filter. A Y-type strainer should also be fitted upstream of the filter to remove all larger particles which would otherwise rapidly block the filter, increase the amount of cleaning required and reduce the life of the filter element.
By installing pressure gauges either side of the filter, the pressure drop across the filter can be measured, which can then be used to identify when the filter requires cleaning. An alternative to this is to install a pressure switch on the downstream side of the filter. When the downstream pressure decreases below a set level, an alarm light can be switched on in a control room alerting an operator who can then clean the filter.

## Slide 33: Steam Distribution System
<number>
Separators remove suspended water droplets from steam
Water in steam causes problems
  Water is barrier to heat transfer
  Erosion of valve seals and fittings and corrosion
  Scaling of pipework and heating surfaces from impurities
  Erratic operation and failure of valves and flow meters
Three types of separators
6. Separators
Notes: <number>
Separators are used to remove suspended water droplets from steam. The presence of water in steam can cause a number of problems:
As water is an extremely effective barrier to heat transfer, its presence can reduce plant productivity and product quality.
Water droplets travelling at high steam velocities will erode valve seals and fittings, a condition known as wiredrawing. The water droplets will also increase the amount of corrosion.
Increased scaling of pipework and heating surfaces from the impurities carried in the water droplets.
Erratic operation of control valves and flow meters.
Failure of valves and flow meters due to rapid wear or water hammer.
There are three types of separators: baffle type, cyclonic type and coalescence type

## Slide 34: Steam Distribution System
<number>
Baffle plates change direction of flow – collect water droplets
Cross-sectional area reduces fluid speed – water droplets fall out of suspension
Condensate in bottom drained away through steam trap
6. Separators – Baffle type
(Spirax Sarco)
Notes: <number>
A baffle or vane type separator consists of a number of baffle plates, which cause the flow to change direction a number of times as it passes through the separator body. The suspended water droplets have a greater mass and a greater inertia than the steam; thus, when there is a change in flow direction, the dry steam flows around the baffles and the water droplets collect on the baffles.
Furthermore, as the separator has a large cross-sectional area, there is a resulting reduction in the speed of the fluid. This reduces the kinetic energy of the water droplets, and most of them will fall out of suspension.
The condensate collects in the bottom of the separator, where it is drained away through a steam trap.

## Slide 35: Steam Distribution System
<number>
Fins generate cyclonic flow
Steam spins around separator body
Water thrown to wall
Drainage through steam trap
6. Separators – Cyclonic type
(Spirax Sarco)
Notes: <number>
The cyclonic or centrifugal type separator uses a series of fins to generate high-speed cyclonic flow. The velocity of the steam causes it to swirl around the body of the separator, throwing the heavier, suspended water to the wall, where it drains down to a steam trap installed under the unit.

## Slide 36: Steam Distribution System
<number>
Wire mesh pad obstructs water molecules
Molecules coalesce into droplets
Large droplets fall to bottom
Drainage through steam trap
6. Separators – Coalescence type
(Spirax Sarco)
Notes: <number>
Coalescence type separators provide an obstruction in the steam path. The obstruction is typically a wire mesh pad (sometimes referred to as a demister pad), upon which water molecules become entrapped. These water molecules tend to coalesce, producing droplets that are too large to be carried further by the gas system. As the size of the droplets increases, they become too heavy and ultimately fall into the bottom of the separator.
It is common to find separators, which combine both coalescence and cyclonic type operations. By combining the two methods, the overall efficiency of the separator is improved.

## Slide 37: Steam Distribution System
<number>
What is a steam trap?
  “Purges” condensate out of the steam system
  Allows steam to reach destination as dry as possible
Steam traps must handle variations in
  Quantity of condensate
  Condensate temperature
  Pressure (vacuum to > 100 bar)
7. Steam traps
Notes: <number>
No steam system is complete without that crucial component 'the steam trap' (or trap). This is the most important link in the condensate loop because it connects steam usage with condensate return. A steam trap quite literally 'purges' condensate, (as well as air and other incondensable gases), out of the system, allowing steam to reach its destination in as dry a state/condition as possible to perform its task efficiently and economically.
The quantity of condensate a steam trap has to deal with may vary considerably. It may have to discharge condensate at steam temperature (i.e. as soon as it forms in the steam space) or it may be required to discharge below steam temperature, giving up some of its 'sensible heat' in the process.
The pressures at which steam traps can operate may be anywhere from vacuum to well over a hundred bar.

## Slide 38: Steam Distribution System
<number>
Selection depends on steam trap’s ability to
Vent air at start-up
Remove condensate but not steam
Maximize plant performance: dry steam
7. Steam traps
Notes: <number>
One type of steam trap cannot possibly be the correct choice for all applications. Considerations for steam trap selection include the ability of the steam trap to:
Vent air at 'start-up', i.e. the beginning of the process when the heater space is filled with air, which unless displaced, will reduce heat transfer and increase the warm-up time
Remove condensate but not the steam
Maximize plant performance. Simply put, unless specifically designed to waterlog, for a heat exchanger to operate at its best performance, the steam space must be filled with clean dry steam. The type of steam trap will influence this.

## Slide 39: Steam Distribution System
<number>
Three groups of steam traps
7. Steam traps
Operated by changes in fluid temperature
Operated by changes in fluid density
Operated by changes in fluid dynamics
Notes: <number>
There are three basic types of steam trap into which all variations fall. All three are classified by International Standard ISO 6704:1982 and include:
(Click once). Thermostatic (operated by changes in fluid temperature). The temperature of saturated steam is determined by its pressure. In the steam space, steam gives up its enthalpy of evaporation (heat), producing condensate at steam temperature. As a result of any further heat loss, the temperature of the condensate will fall. A thermostatic trap will pass condensate when this lower temperature is sensed. As steam reaches the trap, the temperature increases and the trap closes.
(Click once) Mechanical (operated by changes in fluid density). This range of steam traps operates by sensing the difference in density between steam and condensate. These steam traps include 'ball float traps' and 'inverted bucket traps'. In the 'ball float trap', the ball rises in the presence of condensate, opening a valve, which passes the denser condensate. With the 'inverted bucket trap', the inverted bucket floats when steam reaches the trap and rises to shut the valve. Both are essentially 'mechanical' in their method of operation.
(Click once) Thermodynamic (operated by changes in fluid dynamics). Thermodynamic steam traps rely partly on the formation of flash steam from condensate. This group includes 'thermodynamic', 'disc', 'impulse' and 'labyrinth' steam traps.

## Slide 40: Steam Distribution System
<number>
7. Steam traps
Application | Feature | Suitable trap
Steam mains | Open to atmosphere, small capacity Frequent change in pressure Low pressure - high pressure | Thermodynamic, Mechanical: Float
Equipment Reboiler Heater Dryer Heat exchanger etc. | Large capacity Variation in pressure and temperature is undesirable Efficiency of the equipment is a problem | Mechanical: Float Bucket Inverted bucket
Tracer line Instrumentation | Reliability with no over heating | Thermodynamic, Thermostatic: Bimetallic
(BEE India, 2004)
Notes: <number>
As you can see in this table, different types of steam traps are used for different applications.
However, because mechanical steam traps are most commonly used, only these will be described in more detail.

## Slide 41: Steam Distribution System
<number>
Condensate in trap causes ball float to rise – condensate is released
Modern traps use thermostatic air vent to allow initial air to pass
7. Steam traps – Ball float type
(Spirax Sarco)
Float trap with air cock
Float trap with thermostatic air vent
Notes: <number>
We will first explain how the ball float steam trap works
The ball float type trap operates by sensing the difference in density between steam and condensate. In the case of the trap shown in the left figure, condensate reaching the trap will cause the ball float to rise, lifting the valve off its seat and releasing condensate. As can be seen, the valve is always flooded and neither steam nor air will pass through it. An air cock at the top is used to vent air.
Modern traps use a thermostatic air vent, as shown in the right figure. This allows the initial air to pass whilst the trap is also handling condensate.

## Slide 42: Steam Distribution System
<number>
Advantages
  Continuous condensate discharge
  Can handle light or heavy condensate loads
  Can discharge air freely
  Large capacity for its size
  Has steam lock release valve
  Resistance to water hammer
Disadvantages
  Can be damaged by severe freezing
  Different internals needed for varying pressures
7. Steam traps – Ball float type
Notes: <number>
We will now describe the advantages and disadvantages of the ball float steam trap
Advantages of the float-thermostatic steam trap
The trap continuously discharges condensate at steam temperature. This makes it the first choice for applications where the rate of heat transfer is high for the area of heating surface available.
It is able to handle heavy or light condensate loads equally well and is not affected by wide and sudden fluctuations of pressure or flowrate.
As long as an automatic air vent is fitted, the trap is able to discharge air freely.
It has a large capacity for its size.
The versions which have a steam lock release valve are the only type of trap entirely suitable for use where steam locking can occur.
It is resistant to water hammer.
(Click once) Disadvantages of the float-thermostatic steam trap
Although less susceptible than the inverted bucket trap, the float type trap can be damaged by severe freezing and the body should be well lagged, and /or complemented with a small supplementary thermostatic drain trap, if it is to be fitted in an exposed position.
As with all mechanical type traps, different internals are required to allow operation over varying pressure ranges. Traps operating on higher differential pressures have smaller orifices to balance the buoyancy of the float.

## Slide 43: Steam Distribution System
<number>
7. Steam traps – Inverted bucket type
Bucket hangs down
Lever pulls off seat
Condensate flows under bucket and flows away
Steam arrives
Bucket rises and shuts outlet
Steam in bucket condenses or bubbles through vent hole
Main valve opens
Condensate is released
(Spirax Sarco)
Notes: <number>
We will first explain how the inverted bucket steam trap works
(Click once) In (i) the inverted bucket hangs down, pulling the valve off its seat. Condensate flows under the bottom of the bucket filling the body and flowing away through the outlet.
(Click once) In (ii) the arrival of steam causes the bucket to become buoyant, it then rises and shuts the outlet.
(Click once) In (iii) the trap remains shut until the steam in the bucket has condensed or bubbled through the vent hole to the top of the trap body. It will then sink, pulling the main valve off its seat. Accumulated condensate is released and the cycle is repeated.

## Slide 44: Steam Distribution System
<number>
Advantages
  Can withstand high pressures
  Tolerates waterhammer
  Suited for superheated steam lines
  Safer because failure mode is open
Disadvantages
  Slow air discharge
  Trap body must always have enough water
  Check valve needed if pressure fluctuations
  Water seal loss by T superheated steam
  Can be damaged by freezing
7. Steam traps – Inverted bucket type
Notes: <number>
We will now go through the main advantages and disadvantages of this steam trap
Advantages of the inverted bucket steam trap
The inverted bucket steam trap can be made to withstand high pressures.
Like a float-thermostatic steam trap, it has a good tolerance to waterhammer conditions.
Can be used on superheated steam lines with the addition of a check valve on the inlet.
Failure mode is usually open, so it is safer on those applications that require this feature, for example turbine drains.
(Click once) Disadvantages of the inverted bucket steam trap
The small size of the hole in the top of the bucket means that this type of trap can only discharge air very slowly. The hole cannot be enlarged, as steam would pass through too quickly during normal operation.
There should always be enough water in the trap body to act as a seal around the lip of the bucket. If the trap loses this water seal, steam can be wasted through the outlet valve. This can often happen on applications where there is a sudden drop in steam pressure, causing some of the condensate in the trap body to 'flash' into steam. The bucket loses its buoyancy and sinks, allowing live steam to pass through the trap orifice. Only if sufficient condensate reaches the trap will the water seal form again, and prevent steam wastage.
If an inverted bucket trap is used on an application where pressure fluctuation of the plant can be expected, a check valve should be fitted on the inlet line in front of the trap. Steam and water are free to flow in the direction indicated, while reverse flow is impossible, as the check valve would be forced onto its seat.
The higher temperature of superheated steam is likely to cause an inverted bucket trap to lose its water seal. A check valve in front of the trap should be regarded as essential under such conditions. Some inverted bucket traps are manufactured with an integral check valve as standard.
The inverted bucket trap is likely to suffer damage from freezing if installed in an exposed position with sub-zero ambient conditions. As with other types of mechanical traps, suitable lagging can overcome this problem if conditions are not too severe. If ambient conditions well below zero are to be expected, then it may be prudent to consider a more robust type of trap to do the job. In the case of mains drainage, a thermodynamic trap would be the first choice.

## Slide 45: Steam Distribution System
<number>
Waterhammer
  Condensate picked up by moving steam
  Can damage steam trap
  Continuous slope in flow direction reduces this
Dirt
  Affects steam trap performance
Strainers
  Help remove dirt and cheaper than maintaining steam traps
7. Steam traps – considerations
Notes: <number>
a) Waterhammer
Waterhammer is condensate in the steam system that is picked up by moving steam and can cause damage to pipelines, fittings and steam traps. Symptoms of waterhammer are often attributed to malfunction of the steam trap. A more likely explanation is that a faulty steam trap has been damaged by waterhammer. The problem of waterhammer can be eliminated by positioning the pipes so that there is a continuous slope in the direction of flow. A slope of at least 12 mm in every 3 metres is necessary, as also an adequate number of drain points every 30 to 50 metres.
b) Dirt
Dirt is another major factor which must be considered when selecting traps. Although steam condenses to distilled water, it can sometimes contain trace products of boiler feed treatment compound and natural minerals found in water. Pipe dirt created during installation and the products of corrosion also need to be considered.
c) Strainers
These devices are frequently forgotten about in steam systems, often, it seems, in an effort to reduce installation costs. Pipe scale and dirt can affect control valves and steam traps, and reduce heat transfer rates. It is extremely easy and inexpensive to fit a strainer in a pipe, and the low cost of doing so will pay dividends throughout the life of the installation. One thing is certain, strainers are far easier and cheaper to buy and maintain than control valves or steam traps

## Slide 46: Steam Distribution System
<number>
Steam locking
  Can occur in rotating machinery
  Only float trap has ‘steam lock release’ valve
Diffusers
  Installed to end of the pipe
  Reduces sound and ferocity of flash steam discharge
Pipe sizing
  Correct pipe size - traps affected by resistance to flow
  Avoid pipe fittings close to trap – back pressure risk
Air venting
  Important for system warm up and operation
7. Steam traps – considerations
Notes: <number>
d) Steam locking
The possibility of steam locking can sometimes be a deciding factor in the selection of steam traps. It can occur whenever a steam trap is fitted remotely from the plant being drained. It can become acute when condensate is removed through a syphon or dip pipe. To relieve this problem a trap is needed with a 'steam lock release' valve. This is an internal needle valve which allows the steam locked in the syphon pipe to be bled away past the main valve. The float trap is the only type of trap with this facility and is the correct choice on rotating machinery such as drying cylinders.
f) Diffusers
With steam traps draining to atmosphere from open ended pipes, it is possible to see the discharge of hot condensate. A certain amount of flash steam will also be present relative to the condensate pressure before the trap. This can present a hazard to passers by, but the risks can be minimized by reducing the severity of the discharge. This may be achieved by fitting a simple diffuser to the end of the pipe which reduces the ferocity of discharge and sound. Typically, sound levels can be reduced by up to 80%.
h) Pipe sizing
The pipes leading to and from steam traps should be of adequate size. This is particularly important in the case of thermodynamic traps, because their correct operation can be disturbed by excessive resistance to flow in the condensate pipework. Pipe fittings such as valves, bends and tees close to the trap could also cause excessive back pressures and should be avoided.
i) Air venting
When air is carried into the trap space by the steam, the trap function can be affected unless adequate provision is made for removing air either through the steam trap or a separate air vent. If air is not vented properly, the plant can take a long time to warm up and may operate below its potential output.

## Slide 47: Steam Distribution System
<number>
Group trapping
7. Steam traps – considerations
X

(Spirax Sarco)
Notes: <number>
e) Group trapping
Group trapping (Figure above). Group trapping describes the use of one trap serving more than one application. The original reason for group trapping was that there used to be only one kind of steam trap. It was the forerunner of the present day bucket trap, and was very large and expensive. Steam traps today are considerably smaller and cost effective, allowing individual heat exchangers to be properly drained. It is always better for steam using equipment to be trapped on an individual basis rather than on a group basis.
Individual trapping (Figure below). The only satisfactory arrangement is to drain each steam space with own trap and then connect the outlets of the various traps to the common condensate return main.

## Slide 48: Steam Distribution System
<number>
Drain pocket dimensions
7. Steam traps – considerations
(Spirax Sarco)
Notes: <number>
g) Drain point / pockets
The drain point should be large enough and should be located to allow the condensate to flow into the trap easily. For example, a 150 mm steam main will require a drain of at least 100 mm diameter and 150 mm deep located at the bottom of the main. The table on this slide can be used to select the drain point dimensions.

## Slide 49: Steam Distribution System
<number>
Effect of air on heat transfer
8. Air vents
(Spirax Sarco)
Notes: <number>
If air is mixed with steam and flows along with it, pockets of air will remain at the heat exchange surfaces where the steam condenses. Gradually, a thin layer builds up to form an insulating blanket, hindering heat transfer as shown in the figure on this slide.
A film of air only 1 mm thick offers about the same resistance to heat flow as a wall of copper some 15 meters thick!
When air is added to steam, the heat content of a given volume of the mixture is lower than the same volume of pure steam, so the mix temperature is lowered. Hence, the presence of air has a double effect:
  It offers a resistance to heat transfer via its layering effect
  It reduces the temperature of the steam space thus reducing the temperature gradient across the heat transfer surface

## Slide 50: Steam Distribution System
<number>
Air in the system
  During start-up
  Condensing steam draws air in pipes
  In solution in the feedwater
Signs of air
  Gradual fall of output of steam-heated equipment
  Air bubbles in the condensate
  Corrosion
8. Air vents
Notes: <number>
Air is present within steam pipes and steam equipment at start-up. Even if the system were filled with pure steam when used, the condensing steam would cause a vacuum and draw air into the pipes at shutdown. Air can also enter the system in solution in the feedwater. At 80°C, water can dissolve about 0.6 percent of its volume, of air.
Signs of air are:
  A gradual fall off in the output of any steam heated equipment
  Air bubbles in the condensate
  Corrosion

## Slide 51: Steam Distribution System
<number>
Automatic air vent on jacketed pan (vessel)
Automatic air vent on end of main
8. Air vents
(Spirax Sarco)
Notes: <number>
The most efficient means of air venting is with an automatic device. Air mixed with steam lowers the mix temperature. This enables a thermostatic device (based on either the balanced pressure or bimetallic principle) to vent the steam system.
An air vent fitted
  on the steam space of a vessel (top figure) or
  at the end of a steam main (bottom figure) will open when air is present.

## Slide 52: Steam Distribution System
<number>
Within low lying steam trap opposite high level steam inlet
Opposite low level steam inlet
Opposite end of steam inlet
8. Air vent - location
(Spirax Sarco)
Notes: <number>
As an air/steam mixture is denser than pure steam at the same pressure, it is usually sufficient to provide air venting capability within the low-lying steam trap, as shown in the top left figure
(Click once) However, in the case of different steam inlet positions, the location of the air vent could be different. With the bottom steam inlet in the figure on the right, at start-up, air would tend to be pushed to the remote point which is at the top. It may be best to locate an air vent at the top whilst a float-thermostatic steam trap will handle any residual air which has collected at the bottom of the vessel.
(Click once) There may be the need to consider an automatic air vent connected to the steam space above the level of any condensate. Often it is convenient and sufficiently effective to connect it to the top of the steam space, as in the top figure.

## Slide 53: Steam Distribution System
<number>
What is condensate
  Distilled water with heat content
  Discharged from steam plant and equipment through steam traps
Condensate recovery for
  Reuse in boiler feed tank, deaerator or as hot process water
  Heat recovery through heat exchanger
9. Condensate recovery system
Notes: <number>
When a kilogram of steam condenses completely, a kilogram of condensate is formed at the same pressure and temperature. As well as having heat content, the condensate is basically distilled water, which is ideal for use as boiler feedwater.
An efficient steam system will collect this condensate and either return it to a deaerator, a boiler feedtank, or use it in another process. Only when there is a real risk of contamination should condensate not be returned to the boiler. Even then, it may be possible to collect the condensate and use it as hot process water or pass it through a heat exchanger where its heat content can be recovered before discharging the water mass to drain.

## Slide 54: Steam Distribution System
<number>
Reasons for condensate recovery
Financial reasons
Water charges
Effluent restrictions
Maximizing boiler output
9. Condensate recovery system
Notes: <number>
Reasons for condensate recovery include:
Financial reasons: Condensate is a valuable resource and even the recovery of small quantities is often economically justifiable. The discharge from a single steam trap is often worth recovering. Un-recovered condensate must be replaced in the boiler house by cold make-up water with additional costs of water treatment and fuel to heat the water from a lower temperature.
Water charges: Any condensate not returned needs to be replaced by make-up water, incurring further water charges from the local water supplier.
Effluent restrictions: In the UK for example, water above 43°C cannot be returned to the public sewer by law, because it is detrimental to the environment and may damage earthenware pipes. Condensate above this temperature must be cooled before it is discharged, which may incur extra energy costs. Similar restrictions apply in most countries, and effluent charges and fines may be imposed by water suppliers for non-compliance.
Maximizing boiler output: Colder boiler feedwater will reduce the steaming rate of the boiler. The lower the feedwater temperature, the more heat, and thus fuel needed to heat the water, thereby leaving less heat to raise steam.
Boiler feedwater quality: Condensate is distilled water, which contains almost no total dissolved solids (TDS). Boilers need to be blown down to reduce their concentration of dissolved solids in the boiler water. Returning more condensate to the feedtank reduces the need for blowdown and thus reduces the energy lost from the boiler

## Slide 55: Steam Distribution System
<number>
Typical steam and condensate circuit with condensate recovery
9. Condensate recovery system
(Spirax Sarco)
Notes: <number>
An effective condensate recovery system, collecting the hot condensate from the steam using equipment and returning it to the boiler feed system, can pay for itself in a remarkably short period of time.
The figure shows
a simple steam and condensate circuit (point to the top right of the figure)
with condensate returning to the boiler feedtank (point to the bottom left of the figure)

## Slide 56: Steam Distribution System
<number>
Four types of condensate lines
9. Condensate recovery system
(Spirax Sarco)
Notes: <number>
Layout and sizing of condensate return lines are important when installing a condensate recovery system. No single set of recommendations can cover the layout of condensate pipework. Much depends on the application pressure, the steam trap characteristics, the position of the condensate return main relative to the plant, and the pressure in the condensate return main.
The subject of condensate piping will divide naturally into four basic types where the requirements and considerations of each will differ. These four basic types are defined and illustrated in the figure:
  (Click once) Drain line to trap: line carries condensate
  (Click once) Discharge lines from trap: lines carry flash steam
  (Click once) Common return lines: lines carry flash steam
  (Click once) Pumped return line (not shown): line carries condensate

## Slide 57: Steam Distribution System
<number>
Insulator: low thermal conductor that keeps heat confined within or outside a system
Benefits
  Reduced fuel consumption
  Better process control
  Corrosion prevention
  Fire protection of equipment
  Absorbing of vibration
  Protects staff: hot surfaces, radiant heat
10. Insulation
Notes: <number>
A thermal insulator is characterized by a low thermal conductivity and is therefore able to keep heat confined within or outside a system by preventing heat transfer to or from the external environment. Insulation materials are porous and contain a large number of dormant air cells. A large amount of heat energy may be lost without insulation or if insulation is inefficient or improperly installed.
Thermal insulation, by reducing heat loss, delivers the following benefits:
  Reduction of fuel consumption
  Better process control by maintaining process temperatures at a constant level
  Corrosion prevention by keeping the exposed surface of a refrigerated system above dew point
  Fire protection of equipment
  Absorbing of vibration
  Staff working conditions are improved because insulation protects them from exposure to hot surfaces and radiant heat and because insulation reduces noise levels.

## Slide 58: Steam Distribution System
<number>
10. Insulation
Temperature | Application | Materials
Low (<90 oC) | Refrigerators, cold / hot water systems, storage tanks | Cork, wood, 85% magnesia, mineral fibers, polyurethane, expanded polystyrene
Medium (90 – 325 oC) | Low-temperature heating and steam generating equipment, steam lines, flue ducts, | 85% magnesia, asbestos, calcium silicate, mineral fibers
High (>325 oC) | Boilers, super-heated steam systems, oven, driers and furnaces | Asbestos, calcium silicate, mineral fibre, mica, vermiculite, fireclay, silica, ceramic fibre
Classification of insulators
Notes: <number>
Insulators can be classified based on the three temperature ranges for which they are used:
Low Temperature Insulators (up to 90oC), which are used for refrigerators, cold and hot water systems, storage tanks, etc. The most commonly used materials are cork, wood, 85 percent magnesia, mineral fibres, polyurethane and expanded polystyrene
Medium Temperature Insulators (90 – 325oC), which are used in low-temperature heating and steam generating equipment, steam lines, flue ducts, etc. The most commonly used materials include 85 percent magnesia, asbestos, calcium silicate and mineral fibres
High Temperature Insulators (325oC and above), which are typically used for boilers, super-heated steam systems, oven, driers and furnaces. The most commonly used materials are asbestos, calcium silicate, mineral fibre, mica, vermiculite, fireclay, silica and ceramic fibre.

## Slide 59: Steam Distribution System
<number>
Selection criteria
Operating temperature of the system
Type of fuel being fired
Material:
  Resistance to heat, weather, fire/flames
  Thermal conductivity, thermal diffusivity
  Ability to withstand various conditions,
  Permeability
Total cost: material purchase, installing and maintenance
10. Insulation
Notes: <number>
Important factors that should be considered when choosing insulating materials are:
Operating temperature of the system
Type of fuel being fired
Resistance of the materials to heat, weather and adverse conditions
Thermal conductivity of the material
Thermal diffusivity of the material
Ability of the material to withstand the various conditions, such as thermal shock, vibration and chemical attack
Resistance of the material to flames/fire
Permeability of the material
Total cost, including material purchase, installing and maintenance

## Slide 60: Steam Distribution System
<number>
Major source of heat loss
Suitable materials: cork, glass wool, rock wool, asbestos
Also insulate flanges!
10. Insulation
Insulation of steam and condensate lines
Notes: <number>
Insulation of steam and condensate lines
It is essential to insulate steam and condensate pipelines because they are a major source of heat loss through heat radiation from the pipelines. The figure gives an indication of the amount of heat loss from un-insulated pipelines. (Give an example, e.g. the red line represents a 65 m long uninsulated pipeline. At 100 oC the heat loss is 1 MJ/hr. At 200oC the heat loss is 3.5 MJ/hr)
Suitable insulation materials are cork, glass wool, rock wool and asbestos.
Flanges should also be insulated because an uncovered flange is equivalent to leaving 0.6 meter of pipeline un-insulated. Flanges are often not insulated to make it easier to check the condition of the flange. A solution is to install detachable insulation covers, which can be removed when checking the flange.

## Slide 61: Training Agenda: Steam
<number>
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities

## Slide 62: Assessment of Steam Distribution System
<number>
Stream traps
Heat loss from uninsulated surfaces
Condensate recovery
Three main areas of assessment
Notes: <number>
There are many aspects of the steam system that can be assessed. However, there are three areas where assessment is most useful as energy losses, and potential energy savings, are high. These are
Steam traps
Heat losses from un-insulated surfaces
Savings from condensate recovery.
These areas will be discussed as part of Energy Efficiency Opportunities

## Slide 63: Training Agenda: Steam
<number>
Introduction
Steam distribution system
Assessment of steam distribution system
Energy efficiency opportunities

## Slide 64: Energy Efficiency Opportunities
<number>
Manage steam traps
Avoid steam leaks
Provide dry steam for process
Utilize steam at lowest acceptable pressure
Proper utilization of directly injected steam
Minimize heat transfer barriers
Proper air venting
Minimize waterhammer
Insulate pipelines and equipment
Improve condensate recovery
Recover flash steam
Reuse low pressure steam
Notes: <number>
There are many areas for energy efficiency opportunities in the steam distribution system. We will now go through the most important opportunities

## Slide 65: Energy Efficiency Opportunities
<number>
Testing of steam traps
  Visual: flow and flow variations
  Sound: check sound created by flow
  Temperature: discharge temperature on outlet
  Integrated: measures conductivity
Routine maintenance
Replacement of internal parts
Replacement of traps
1. Manage steam traps
Notes: <number>
Energy losses can be reduced using steam traps, provided attention is giving to the following areas:
Testing of steam traps (the text on the slides should be sufficient for the session. The full text from the book is included below but it depends on time whether all information can be explained)
  Visual: Visual testing of the flow or variation of flow of steam traps makes use of sight glasses, sight checks, test tees and three-way test valves. This method works well with traps that have an on/off cycle or low flows. This method becomes less viable when the flow, and thus the volume of water and flash steam, is high
  Sound: Sound testing makes use of ultrasonic leak detectors, mechanics stethoscopes, screwdriver or a metal listening rod. These methods use the sound created by flow to determine if the trap is functioning properly. This method works well with traps that have an on/off cycle or low flows, but not so well with traps with varying and/or high flows
  Temperature: Temperature testing makes use of infrared guns (see Monitoring Equipment chapter), surface pyrometers, temperature tapes, and temperature crayons. These equipment measure the discharge temperature on the outlet side of the trap, with high temperatures indicating leaks and low temperatures indicating blocked, undersized, or faulty traps.
  Integrated: Spirax Sarco mentions the development of an integrated steam trap testing device due to the limitations of the above methods. This consists of a sensor, fitted inside the steam trap, which is capable of detecting the physical state of the medium at that point by conductivity. This
Routine maintenance, which depends on the type of trap and its application.
Replacement of internals. The renewal of internal parts of a steam trap makes good sense. The body will generally have as long a life as the plant to which it is fitted and it is only the internal parts which wear, depending on system conditions. There are obvious advantages in replacing these internals from time to time. It depends on the ease with which the new parts can be fitted and the reliability and availability of the refurbished trap.
Replacement of traps. On occasions, it will be easier and cheaper to replace traps rather than repair them. In these cases it is essential that the traps themselves can be changed easily. Flanged connections provide one solution, although the flanged trap is more expensive than the equivalent screwed trap. Mating flanges are an additional expense.

## Slide 66: Energy Efficiency Opportunities
<number>
Repair leaks
Regular leak detection program
Replace flanged joints by welded joints
Leakage estimate
  Plume length 1400 mm
  Steam loss 40 kg/hr
2. Avoid steam leaks
Notes: <number>
Steam leaks are a source of energy loss and must be avoided.
It is estimated that a 3 mm diameter hole on a pipeline carrying 7kg/cm2 steam would waste 33 kL of fuel oil per year.
Steam leaks on high-pressure mains are prohibitively costlier than on low pressure mains.
T avoid steam leaks, a plant should
Repair leaks immediately
Have a regular surveillance programme for identifying leaks at pipelines, valves, flanges and joints.
Replace the flanged joints which are rarely opened in old plants by welded joints.
(Click once) The figure provides a quick estimate for steam leakage based on plume length. For example, if the plume length is 700 mm then the steam loss is 10 kg/h

## Slide 67: Energy Efficiency Opportunities
<number>
Dry saturated steam is best steam
  Wet steam reduces total heat in steam and prevents heat transfer
  Superheated steam gives up heat at slower rate
Achieve dry steam by
  Proper boiler treatment
  Boiler operation
  Pipeline insulation
  Separators on steam pipelines
3. Provide dry steam for process
Notes: <number>
The best steam for industrial process heating is the dry saturated steam.
  Wet steam reduces total heat in the steam. Also water forms a wet film on heat transfer and overloads traps and condensate equipment. Wet steam can reduce plant productivity and product quality, and can cause damage to most items of plant and equipment.
  Superheated steam is not desirable for process heating because it gives up heat at a rate slower than the condensation heat transfer of saturated steam.
It must be remembered that a boiler without a superheater cannot deliver perfectly dry saturated steam. At best, it can deliver only 95 to 98 percent dry steam. The dryness fraction of steam depends on various factors, such as the level of water in the boiler. The dryness of the steam can be maximized by
  Proper boiler water treatment
  Boiler operation
  Lagging of the pipelines
  Separators in steam pipelines to remove suspended water droplets, separators are installed in steam pipelines

## Slide 68: Energy Efficiency Opportunities
<number>
Steam should be
  Generated & distributed at highest pressure
  Utilized at lowest pressure: latent heat highest
Select lowest steam pressure without sacrificing
  Production time
  Steam consumption
4. Utilize steam at lowest acceptable pressure
Notes: <number>
4. Utilize steam at the lowest acceptable pressure for the process
As a guide, the steam should always be generated and distributed at the highest possible pressure, but utilized at as low a pressure as possible since it then has higher latent heat.
There is a limit to the reduction of steam pressure. Depending on the equipment design, the lowest possible steam pressure with which the equipment can work should be selected without sacrificing
  Production time: it may also be seen from the steam tables that the lower the steam pressure, the lower will be its temperature. Since temperature is the driving force for the transfer of heat at lower steam pressures, the rate of heat transfer will be slower and the processing time greater
  Steam consumption: In equipment where fixed losses are high (e.g. big drying cylinders), there may even be an increase in steam consumption at lower pressures due to increased processing time.

## Slide 69: Energy Efficiency Opportunities
<number>
Benefits
  Equipment simple, cheap and easy to maintain
  No condensate recovery system needed
  Heating quick and process thermally efficient
Only in processes were dilution is not a problem
5. Proper utilization of directly injected steam
Notes: <number>
5. Proper utilization of directly injected steam
The heating of a liquid by direct injection of steam is often desirable.
The equipment required is relatively simple, cheap and easy to maintain.
No condensate recovery system is necessary.
The heating is quick, and the sensible heat of the steam is also used up along with the latent heat, making the process thermally efficient.
In processes where dilution is not a problem, heating is done by blowing steam into the liquid, i.e. direct steam injection is applied. If the dilution of the tank contents and agitation are not acceptable in the process, i.e. direct steam agitation is not acceptable, indirect steam heating is the only answer.

## Slide 70: Energy Efficiency Opportunities
<number>
Temperature gradient across heat transfer barriers
6. Minimize heat transfer barriers
(Spirax Sarco)
Notes: <number>
6. Minimize heat transfer barriers
Heat transfer barrier are shown in the figure: The metal wall may not be the only barrier in a heat transfer process. There is likely to be a film of air, condensate and scale on the steam side. On the product side there may also be baked-on product or scale, and a stagnant film of product. (Point at each barrier on the figure)

## Slide 71: Energy Efficiency Opportunities
<number>
Possible solutions
Stagnant film: product agitation
Scale
  Regular product cleaning
  Regular surface cleaning on steam side
  Correct operation of boiler
  Removal of water droplets with impurities
Condensation: coat that inhibits wetting
Air: air venting
6. Minimize heat transfer barriers
Notes: <number>
Possible solutions:
Stagnant film: Agitation of the product may eliminate the effect of the stagnant film
Scale:
Regular cleaning on the product side should reduce the scale.
Regular cleaning of the surface on the steam side may also increase the rate of heat transfer by reducing the thickness of any layer of scale, however, this may not always be possible.
This layer may also be reduced by careful attention to the correct operation of the boiler, and the removal of water droplets carrying impurities from the boiler.
Condensation: A condensate film may be between 100 and 150 times more resistant to heat transfer than a steel heating surface, and 500 to 600 times more resistant than copper. If the droplets of water on the heat transfer surface do not merge immediately, ‘dropwise’ condensation occurs which has higher heat transfer rates. If the surface is coated with a substance that inhibits wetting (Silicones, PTFE and an assortment of waxes and fatty acids), it may be possible to maintain dropwise condensation for a period of time. However, these coatings will gradually lose their effectiveness due to processes such as oxidation or fouling, and film condensation will eventually predominate.
Air: air venting, which was already explained as a component of the steam distribution system (Note: number 7 “Proper air venting” is for this reason not discussed again)

## Slide 72: Energy Efficiency Opportunities
<number>
Banging noise caused by colliding condensate in distribution system
Sources: low points in the pipework
Solutions
  Steam lines with gradual fall in flow direction
  Drain points at regular intervals
  Check valves after all steam traps
  Opening isolation valves slowly to drain condensate
8. Minimize waterhammer
Notes: <number>
Waterhammer is the noise caused by slugs of condensate colliding at high velocity into pipework fittings, plant, and equipment.
Indications of waterhammer include a banging noise, and perhaps movement of the pipe. In severe cases, waterhammer may fracture pipeline equipment with almost explosive effect, with consequent loss of live steam at the fracture, leading to an extremely hazardous situation.
Commonly, sources of waterhammer occur at the low points in the pipework, for example, sagging in the line, perhaps due to failure of supports.
To summarize, the possibility of waterhammer is minimized by:
  Installing steam lines with a gradual fall in the direction of flow, and with drain points installed at regular intervals and at low points.
  Installing check valves after all steam traps, which would otherwise allow condensate to run back into the steam line or plant during shutdown.
  Opening isolation valves slowly to allow any condensate, which may be lying in the system to flow gently through the drain traps, before it is picked up by high velocity steam. This is especially important at start-up.

## Slide 73: Assessment of Steam Distribution System
<number>
9. Insulation
Costs of insulation
Heat loss savings
Economic Thickness of Insulation (ETI)
Notes: <number>
What insulation is, the benefits and types of insulation options were already explained as part of the steam distribution system. An important factor in determining if insulation or improved insulation is a good energy efficiency option is the costs. For this reason we will explain how to determine if insulation is cost effective.
The effectiveness of insulation follows the law of decreasing returns. This means that insulation results in energy and cost savings, but with increasing thickness of insulation the additional amount of energy and cost saved is going down.
The figure shows this:
(Click once) the costs of insulation per m2 of surface rises with increasing insulation thickness
(Click once) the heat savings per m2 of insulated surfaces decreases with increasing insulation thickness
(Click once) At a certain level, any additional insulation is no longer economically justifiable. The point where the amount of insulation gives the greatest return on investment is called the “economic thickness of insulation” (ETI) and is shown in the figure.
The ETI is calculated based on the following factors, which differ between companies:
Cost of fuel
Annual hours of operation
Heat content of fuel
Boiler efficiency
Operating surface temperature
Pipe diameter/thickness of surface
Estimated cost of insulation.
Average exposure ambient still air temperature
Note: a calculation method (section 3.2.2) and example (section 3.2.3) is included in the chapter but will not be explained as part of this session

## Slide 74: Assessment of Steam Distribution System
<number>
10. Improved condensate recovery
Annual condensate recovered (kg/yr)
Heat recovered (kcal/yr)
Heat saved (kcal/yr)
Fuel saved (litres or m3 /yr)
$ saved ($ /yr)
Notes: <number>
Calculating the amount of money saved from condensate recovery allows you to determine further potential savings from improved condensate recovery.
The savings from condensate recovery can be calculated as follows:
Calculate the annual quantity of condensate recovered in kg/yr
Calculate the heat recovered by converting the kg/yr to kcal/yr
Calculate the heat saved in kcal/yr by multiplying the heat recovered by the boiler efficiency, e.g. 80%
Calculate the amount of fuel (coal, fuel oil or gas) saved by multiplying the heat saved with the calorific value of fuel
Calculate the amount of money saved by multiplying the amount of fuel with the cost of fuel

## Slide 75: Energy Efficiency Opportunities
<number>
Energy in condensate lower than energy in steam but worth recovering:
Every 6oC rise in the feed water temperature = 1% fuel savings in the boiler
10. Improved condensate recovery
(Spirax Sarco)
Notes: <number>
The figure compares the amount of energy in a kilogram of steam and condensate at the same pressure. The percentage of energy in condensate to that in steam can vary from 18 percent at 1 bar g to 30 percent at 14 bar g. Clearly the liquid condensate is worth reclaiming. If this water is returned to the boiler house, it will reduce the fuel requirements of the boiler. For every 6oC rise in the feed water temperature, there will be approximately 1 percent saving of fuel in the boiler.

## Slide 76: Energy Efficiency Opportunities
<number>
Flash steam released from hot condensate when pressure reduced
Amount available: calculation or tables/charts
Applications: heating
Boiler blowdown can also be recovered as flash steam
11. Recover flash steam
Notes: <number>
Flash steam is released from hot condensate when its pressure is reduced. As an example, when steam is taken from a boiler and the boiler pressure drops, some of the water content of the boiler will flash off to supplement the ‘live’ steam produced by the heat from the boiler fuel.
If use is to be made of flash steam, it is helpful to know how much of it will be available. The quantity is readily determined by calculation, or can be read from simple tables or charts.
Typical applications of flash steam include heating (with air heater batteries and space heating installations using either radiant panels or unit heaters), steam heated hot water calorifier and a steam to water calorifier. Boiler blowdown can also be recovered as flash steam, as is explained in the separate Boiler Chapter.

## Slide 77: Energy Efficiency Opportunities
<number>
Reuse as water
Compress with high pressure steam for reuse as medium pressure steam
12. Reuse low pressure steam
MOTIVE STEAM H.P.
DISCHARGE STEAM
M.P.
SUCTION STEAM L.P.
Thermo-compressor
Notes: <number>
In many cases, very low pressure steam is reused as waIn many cases, very low pressure steam is reused as water after condensation when there is no better reuse option. In many cases it becomes feasible to compress this low pressure steam with very high pressure steam and reuse it as a medium pressure steam. The major energy in steam is in its latent heat value and thus thermo-compression would give a large improvement in waste heat recovery. The thermo-compressor (Figure 50) is a simple equipment with a nozzle where HP steam is accelerated into a high velocity fluid. This entrains the LP steam by momentum transfer and then recompresses in a divergent venturi. It is typically used in evaporators where the boiling steam is recompressed and used as heating steam.ter after condensation when there is no better reuse option.
In many cases it becomes feasible to compress this low pressure steam with very high pressure steam and reuse it as a medium pressure steam. The major energy in steam is in its latent heat value and thus thermo-compression would give a large improvement in waste heat recovery.
The thermo-compressor (see figure) is a simple equipment with a nozzle where HP steam is accelerated into a high velocity fluid. This entrains the LP steam by momentum transfer and then recompresses in a divergent venturi. It is typically used in evaporators where the boiling steam is recompressed and used as heating steam.

## Slide 78: Training Session on Energy Equipment
<number>
Steam Distribution and Utilization
THANK YOU
FOR YOUR ATTENTION

## Slide 79: Disclaimers and References
<number>
This PowerPoint training session was prepared as part of the project “Greenhouse Gas Emission Reduction from Industry in Asia and the Pacific” (GERIAP). While reasonable efforts have been made to ensure that the contents of this publication are factually correct and properly referenced, UNEP does not accept responsibility for the accuracy or completeness of the contents, and shall not be liable for any loss or damage that may be occasioned directly or indirectly through the use of, or reliance on, the contents of this publication. © UNEP, 2006.
The GERIAP project was funded by the Swedish International Development Cooperation Agency (Sida)
Many sections of this chapter were taken from, based on or are a summary of modules featured in Spirax Sarco’s web-based Learning Centre with the kind permission of Spirax Sarco. For more detailed information please refer to www.spiraxsarco.com/learn. Full references are included in the textbook chapter that is available on www.energyefficiencyasia.org
Spirax Sarco copyright and disclaimer: Spirax Sarco cannot be held responsible for any mishap, or misinterpretation of this technical material, or out-of-date technical material, or any claim by any person or persons or organisations as a result of this information as printed in this document, either expressed or implied, and whether in hard copy or electronic copy. The Spirax Sarco technical material used in this document is copyright of Spirax Sarco and remains the full and exclusive intellectual property of Spirax Sarco at all times.